Wiring and Pin List

Field Sensor Hub, Central Control Station and Power Actuation Panel

Development of Soil Moisture-Based Automated Irrigation and Fertigation for the Garden of Roxas City School for Philippine Craftsmen

Date: 2026-10-14

# 1. Overview

- The field sensor hub (Arduino Nano) reads four soil moisture sensors on A0 to A3 and sends one line, "bed1,bed2" (percent), every 5 seconds over RS485 at 9600 baud, 8N1.

- The central control station (ESP32-S3) receives that line on GPIO 16.

- On the ESP32 side, everything that runs at 5 V (both LCDs, the relay inputs and the flow sensor signal) goes through two 4-channel level shifter boards.

- Bed 1 = sensors A and B. Bed 2 = sensors C and D.

- The 220 V power actuation panel (breaker, contactor, pump, solenoid valves and outlet) is in section 8.

# 2. Power and ground

| Supply | Powers | Notes | OK |
| --- | --- | --- | --- |
| Field hub 5 V supply | Arduino Nano | Nano 5V pin feeds the MAX485 module and the four sensors. | ☐ |
| ESP32 5 V adapter | ESP32-S3 (USB port) | ESP32 3V3 pin feeds the RS485 transceiver and the LV pin of both level shifters. | ☐ |
| 5 V adapter, 1 A or more | Relay module, both LCDs, flow sensor, HV pin of both level shifters | About 500 mA in total, so do not use a weak adapter. | ☐ |

- Join all grounds in the central station on one terminal block: ESP32, relay module, LCDs, flow sensor, both level shifters and the cable GND wire.

- Never connect the + (5 V) wires of two adapters together. Only the grounds are joined.

# 3. Field sensor hub (Arduino Nano)

## 3.1 Nano pins

| Nano pin | Connects to | Notes | OK |
| --- | --- | --- | --- |
| A0 | Sensor A, AOUT | Bed 1 | ☐ |
| A1 | Sensor B, AOUT | Bed 1 | ☐ |
| A2 | Sensor C, AOUT | Bed 2 | ☐ |
| A3 | Sensor D, AOUT | Bed 2 | ☐ |
| TX1 | MAX485 module, RXD | Data out. Crossed: Nano TX goes to module RXD. | ☐ |
| RX0 | MAX485 module, TXD | Optional, the Nano never listens. | ☐ |
| 5V | MAX485 VCC and the four sensor VCC wires | Shared 5 V | ☐ |
| GND | Terminal block (common ground) |  | ☐ |

Unplug TX1 and RX0 whenever you upload code to the Nano. Set DEBUG = false in the sketch so only the "bed1,bed2" line is sent.

## 3.2 MAX485 module (field end)

| Module pin | Connects to | Notes | OK |
| --- | --- | --- | --- |
| VCC | Nano 5V |  | ☐ |
| GND | Terminal block (ground) |  | ☐ |
| RXD | Nano TX1 |  | ☐ |
| TXD | Nano RX0 | Optional | ☐ |
| A+ | Cable wire A+ |  | ☐ |
| B- | Cable wire B- |  | ☐ |

## 3.3 Each soil moisture sensor (one Cat6 cable each, 15 ft)

| Sensor pin | Cat6 wire | Goes to | OK |
| --- | --- | --- | --- |
| AOUT | Orange | Nano A0, A1, A2 or A3 | ☐ |
| GND | White-orange | Terminal block (ground) | ☐ |
| VCC | Green | 5 V | ☐ |
| GND (second) | White-green | Terminal block (ground), tied to the first GND at both ends | ☐ |

At each sensor: 100 µF, 16 V capacitor across VCC and GND, striped leg (−) on GND. Keep the same color order at both ends of the cable. The blue and brown pairs are unused. Keep the cables away from the pump, contactor and mains wiring.

# 4. RS485 cable between the hub and the station

| Wire | Field hub end | Central station end | OK |
| --- | --- | --- | --- |
| A+ | MAX485 module A+ | Transceiver A+ | ☐ |
| B- | MAX485 module B- | Transceiver B- | ☐ |
| GND | Terminal block ground | Common ground terminal block | ☐ |

Use one twisted pair for A+ and B-, and a separate wire for GND. Match the letters at both ends: A to A and B to B.

# 5. Central control station (ESP32-S3)

## 5.1 ESP32 pin list

| GPIO | Function | Connects to | Through | OK |
| --- | --- | --- | --- | --- |
| 16 | RS485 receive (Serial2 RX) | Transceiver TXD | Direct | ☐ |
| 17 | RS485 transmit (Serial2 TX) | Transceiver RXD | Direct | ☐ |
| 8 | I2C SDA | SDA of both LCDs | Level shifter A, ch 1 | ☐ |
| 9 | I2C SCL | SCL of both LCDs | Level shifter A, ch 2 | ☐ |
| 5 | Flow sensor signal | Flow sensor yellow wire | Level shifter A, ch 3 | ☐ |
| 15 | Relay 1 (pump contactor) | Relay module IN1 | Level shifter B, ch 1 | ☐ |
| 2 | Relay 2 (solenoid valve 1) | Relay module IN2 | Level shifter B, ch 2 | ☐ |
| 4 | Relay 3 (solenoid valve 2) | Relay module IN3 | Level shifter B, ch 3 | ☐ |
| 14 | Toggle switch: Irrigation | Switch, other end to GND | Direct, INPUT_PULLUP | ☐ |
| 13 | Toggle switch: Fertigation | Switch, other end to GND | Direct, INPUT_PULLUP | ☐ |
| 12 | Toggle switch: Manual | Switch, other end to GND | Direct, INPUT_PULLUP | ☐ |
| 11 | Toggle switch: Solenoid 1 | Switch, other end to GND | Direct, INPUT_PULLUP | ☐ |
| 10 | Toggle switch: Solenoid 2 | Switch, other end to GND | Direct, INPUT_PULLUP | ☐ |

GPIO 8 and 9 are the ESP32-S3 default I2C pins in the Arduino core. If your code sets other pins, use those instead. Match each switch to its pin number in your code. Relay modules are active-low.

## 5.2 ESP32 power pins

| ESP32 pin | Connects to | OK |
| --- | --- | --- |
| 3V3 | RS485 transceiver VCC and the LV pin of both level shifters | ☐ |
| GND | Common ground terminal block | ☐ |
| USB port | Its own 5 V adapter | ☐ |

## 5.3 RS485 transceiver (central end)

| Module pin | Connects to | Notes | OK |
| --- | --- | --- | --- |
| VCC | ESP32 3V3 | Power it from 3.3 V, not 5 V. | ☐ |
| GND | Common ground |  | ☐ |
| TXD | ESP32 GPIO 16 |  | ☐ |
| RXD | ESP32 GPIO 17 |  | ☐ |
| A+ | Cable wire A+ |  | ☐ |
| B- | Cable wire B- |  | ☐ |

# 6. Level shifters (two 4-channel boards)

On both boards: HV to the 5 V adapter (+), LV to ESP32 3V3, and GND to the common ground. The ESP32 connects to the LV side. The devices connect to the HV side.

## Board A: LCDs and flow sensor

| Channel | LV side (ESP32) | HV side (device) | OK |
| --- | --- | --- | --- |
| 1 | GPIO 8 (SDA) | SDA of both LCDs | ☐ |
| 2 | GPIO 9 (SCL) | SCL of both LCDs | ☐ |
| 3 | GPIO 5 | Flow sensor yellow wire | ☐ |
| 4 | Not used | Not used | ☐ |

## Board B: relay inputs

| Channel | LV side (ESP32) | HV side (device) | OK |
| --- | --- | --- | --- |
| 1 | GPIO 15 | Relay module IN1 | ☐ |
| 2 | GPIO 2 | Relay module IN2 | ☐ |
| 3 | GPIO 4 | Relay module IN3 | ☐ |
| 4 | Not used | Not used (IN4 unused) | ☐ |

The shifter boards hold each relay input high while the ESP32 starts up, so the relays stay off during boot.

# 7. Devices on the 5 V adapter

## Both LCDs (20x4, I2C)

| LCD pin | Connects to | Notes | OK |
| --- | --- | --- | --- |
| VCC | 5 V adapter (+) |  | ☐ |
| GND | Common ground |  | ☐ |
| SDA | Level shifter A, HV1 | Both LCDs on the same wire | ☐ |
| SCL | Level shifter A, HV2 | Both LCDs on the same wire | ☐ |

Addresses: 0x27 shows Bed 1. 0x26 (A0 jumper soldered) shows Bed 2. Turn the blue contrast knob on each backpack for the best text, and keep the backlight jumper on.

## Flow sensor

| Wire | Connects to | OK |
| --- | --- | --- |
| Red | 5 V adapter (+) | ☐ |
| Black | Common ground | ☐ |
| Yellow | Level shifter A, HV3 | ☐ |

## Relay module (4-channel)

| Module pin | Connects to | Notes | OK |
| --- | --- | --- | --- |
| VCC | 5 V adapter (+) | Leave the JD-VCC jumper in place. | ☐ |
| GND | Common ground |  | ☐ |
| IN1 | Level shifter B, HV1 | Pump contactor | ☐ |
| IN2 | Level shifter B, HV2 | Solenoid valve 1 | ☐ |
| IN3 | Level shifter B, HV3 | Solenoid valve 2 | ☐ |
| IN4 | Not connected |  | ☐ |

## Toggle switches (5)

Each switch has two wires: one to its ESP32 GPIO (14, 13, 12, 11 or 10) and the other to GND. Closed (ON) pulls the pin to ground. No resistor is needed.

# 8. Power actuation panel (220 V AC)

This part is mains voltage. Switch the breaker off before you change any wire, and keep every terminal covered or inside an enclosure.

## 8.1 Supply and breaker

| Item | Connects to | Notes | OK |
| --- | --- | --- | --- |
| 220 V supply, Live (L) | 2P breaker, input pole 1 | 2P, 16 A, AC-rated breaker | ☐ |
| 220 V supply, Neutral (N) | 2P breaker, input pole 2 |  | ☐ |
| Breaker output pole 1 (Live) | Contactor L1, relay K1 COM and the 4-gang outlet live | Join with a terminal block | ☐ |
| Breaker output pole 2 (Neutral) | Contactor L2, contactor coil A2 and the 4-gang outlet neutral | Join with a terminal block | ☐ |

## 8.2 Contactor (CJX2-3210)

| Terminal | Connects to | Notes | OK |
| --- | --- | --- | --- |
| L1 (1) | Breaker output, Live | Power pole in | ☐ |
| L2 (3) | Breaker output, Neutral | Power pole in | ☐ |
| T1 (2) | Pump live wire | Power pole out | ☐ |
| T2 (4) | Pump neutral wire | Power pole out | ☐ |
| L3 (5), T3 (6), 13/14 NO | Not used | Leave empty | ☐ |
| A1 (coil) | Relay K1, NO terminal |  | ☐ |
| A2 (coil) | Breaker output, Neutral |  | ☐ |
| Snubber module | Across A1 and A2 | Protects the relay contacts | ☐ |

Check the coil voltage printed near A1 and A2. This wiring assumes a 220 V AC coil. If the coil is a different voltage, do not connect it to mains.

## 8.3 Relay module outputs (K1 to K4)

| Relay | COM | NO | Switches | OK |
| --- | --- | --- | --- | --- |
| K1 | Live from the breaker output | Contactor coil A1 | Pump contactor | ☐ |
| K2 | 12 V adapter (+) | Solenoid valve 1 (+) | Valve 1 | ☐ |
| K3 | 12 V adapter (+) | Solenoid valve 2 (+) | Valve 2 | ☐ |
| K4 | Not used | Not used |  | ☐ |

Each valve (−) wire goes to the 12 V adapter (−), with a snubber module across each valve. K1 carries 220 V, so keep its wires apart from the low-voltage wiring. Relay contacts are rated 10 A, 250 VAC.

## 8.4 Pump and outlet

| Item | Connects to | Notes | OK |
| --- | --- | --- | --- |
| Pump live wire | Contactor T1 |  | ☐ |
| Pump neutral wire | Contactor T2 |  | ☐ |
| Pump earth | Not used if the pump is double-insulated | Square-in-a-square symbol on the nameplate. If the pump has a metal body or an earth pin, connect earth. | ☐ |
| 4-gang outlet | Breaker output, Live and Neutral | Feeds the 12 V adapter, the 5 V relay and LCD adapter, and the 5 V ESP32 adapter | ☐ |

## 8.5 Mains checklist

☐  Breaker is switched off before any wiring is changed.

☐  Breaker is AC-rated, 2P, 16 A.

☐  Wire is 2.5 mm² or larger for the breaker, contactor and pump circuit, with ferrules on stranded wire.

☐  Every screw terminal is tight and no loose strands are showing.

☐  Contactor, relay terminals and outlet wiring are covered or in an enclosure.

☐  Click test first, with L1, L2 and the pump unwired: the contactor pulls in and releases cleanly.

☐  The pump has water before it is switched on.

☐  A qualified person has inspected the mains wiring.

Mains wiring inspected by: ______________________________        Date: ____________________

# 9. First power-up checklist (low-voltage side)

☐  With all adapters unplugged, use the multimeter beep mode to check that every ground is joined.

☐  Plug in the 5 V relay and LCD adapter. Measure about 5 V at the HV pins of both shifters.

☐  Plug in the ESP32. Measure about 3.3 V at the LV pins of both shifters.

☐  The relays must stay off while the ESP32 starts and while you upload code.

☐  Both LCDs show text. Adjust the contrast knobs. Check the addresses 0x27 and 0x26.

☐  Spin or blow through the flow sensor and check that the flow reading changes.

☐  The ESP32 Serial Monitor shows a "bed1,bed2" line every 5 seconds. If you see nothing or garbage, swap the RXD and TXD wires on the module and check A+ and B- are not swapped.

☐  Flip each toggle switch and check that its input changes.

Checked by: ______________________________        Date: ____________________